## Gen. coolers
Doc No.: OMSB 008-00 |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS | UNIT | Time | [5 empty] | Normal Range
[5 empty] | 0 | 4 | 8 | 12 | 16 | 20
UNIT IN: OPER/TURN/STANDSTILL | [10 empty] | OP / TG / SS
Actual Load |  |  | MBY10CE901 | MW | [6 empty] | 0<MW<180
Gen. coolers | Gen. cooler 1 outlet temp |  | MPR30CT501 | ºc | [6 empty] | 10<T<45
| Gen. cooler 2 outlet temp |  | MPR30CT502 | ºc | [6 empty] | 10<T<45
| Gen. cooler 3 outlet temp |  | MPR30CT503 | ºc | [6 empty] | 10<T<45
| Gen. cooler 4 outlet temp |  | MPR30CT504 | ºc | [6 empty] | 10<T<45
| Gen cooler 1 DP |  | MPR20CP501 | mbar | [6 empty] | DP<2000
| Gen cooler 2 DP |  | MPR20CP502 | mbar | [6 empty] | DP<2000
| Gen cooler 3 DP |  | MPR20CP503 | mbar | [6 empty] | DP<2000
| Gen cooler 4 DP |  | MPR20CP504 | mbar | [6 empty] | DP<2000
| GEN lube oil CE Return Press |  | MBV90CP405 | bar | [6 empty] | P >1.8
| GEN lube oil OCE Return Press |  | MBV90CP404 | bar | [6 empty] | P >1.8
NIGHT SHIFT |  |  | DAY SHIFT |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER | OPERATOR | ENGINEER |  | OPERATOR |  | ENGINEER

## SLIP RING
Doc No.: OMSB 008-00 |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | STATE | Time | [5 empty] | Normal Range
|  |  |  | 0 | 4 | 8 | 12 | 16 | 20
SLIP RING | SLIP RING( NOISE) |  | OK / NOK | [6 empty] | OK
| BRUSHES FLEXIBLE CONNECTION |  | OK / NOK | [6 empty] | OK
| SLIP RING( CLEANING) |  | OK / NOK | [6 empty] | OK
| SLIP RING( ARC) |  | OK / NOK | [6 empty] | OK
NIGHT SHIFT |  |  | DAY SHIFT |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER | OPERATOR | ENGINEER |  | OPERATOR |  | ENGINEER

## LUBE OIL SKID
Doc No.: OMSB 008-00 |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS |  | UNIT | Time | [5 empty] | Normal Range
[6 empty] | 0 | 4 | 8 | 12 | 16 | 20
LUBE OIL SKID | Main Lube Oil Pump Disch. Press |  | MBV21CP501 |  | bar | [6 empty] | >5.5
| Lube Oil Filter ΔP |  | MBV25CP001 |  | % | [6 empty] | <40%
| Lube Oil Press After Filter |  | MBV26CP501 |  | bar | [6 empty] | P>1.7
| Lube Oil Tank Vacuum press. |  | MBV50CP501 |  | mbar | [6 empty] | -5.5<P<-6.5
| Lube Oil Filter In Service |  | MBV25AT001 |  | 1/2 | [6 empty] | 1/2
| GT Jacking Discharge Press. |  | MBV30CP502 |  | bar | [6 empty] | P>150
| Gen Jacking Discharge Press. |  | MBV35CP501 |  | bar | [6 empty] | P>250
| Comp. Bear jack. Press. |  | MBV31CP502 |  | bar | [6 empty] | 90<P<100
| GT. Bear Jack. Press |  | MBV31CP501 |  | bar | [6 empty] | 90<P<100
| Gen. CE Bear Jack. Press |  | MBV35CP504 |  | bar | [6 empty] | 90<P<100
| Gen. OCE Bear Jack. Press |  | MBV35CP503 |  | bar | [6 empty] | 90<P<100
| Lube Oil Tank Temp |  | MBV10CT501 |  | ºc | [6 empty] | 35<T<75
| Lube Oil Tank Level |  | MBV10CL501 |  | L/N/H | [6 empty] | Normal
| Sound Of Motors |  | - |  | Normal | [6 empty] | Normal
| Leakage And Cleaning |  | - |  | Ok/not ok | [6 empty] | OK
LUBE OIL COOLER | Cooler In Service |  | MBV23AH001 |  | 1/2 | [6 empty] | 1/2
MBV23AH002
| Lube Oil Inlet Temp. |  | MBV23CT511 |  | ºc | [6 empty] | 60<T<70
MBV23CT521
| Lube Oil Inlet Press. |  | MBV23CP511 |  | bar | [6 empty] | 5<P<6
MBV23CP521
| Lube Oil Outlet Temp. |  | MBV23CT512 |  | ºc | [6 empty] | 15<T<48
MBV23CT522
| Lube Oil Outlet Press. |  | MBV23CP512 |  | bar | [6 empty] | 4<P<6
MBV23CP521
| Water Inlet Cooler Temp. |  | MBV23CT513 |  | ºc | [6 empty] | T OUT >T inlet +5
MBV23CT523
| Water Inlet Cooler Press. |  | MBV23CP513 |  | bar | [6 empty] | P>3
MBV23CP523
| Water Outlet Cooler Temp. |  | MBV23CT514 |  | ºc | [6 empty] | T OUT >T inlet +5
MBV23CT524
| Water Outlet Cooler Press. |  | MBV23CP514 |  | bar | [6 empty] | 1.8<P<2.2
MBV23CP524
| Leakage |  | - |  | OK/NOT OK | NOT OK | [5 empty] | ok
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## HYDR.SKID
Doc No.: OMSB 008-00 |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS |  | UNIT | Time | [5 empty] | Normal Range
[6 empty] | 0 | 4 | 8 | 12 | 16 | 20
HYDR.SKID | Hyd. Pump 1 Press. |  | MBX07CP501 |  | bar | [6 empty] | 165>P>155
| Hyd. Pump 2 Press. |  | MBX07CP511 |  | bar | [6 empty] | 165>P>155
| Hyd. Oil Press. |  | MBX07CP502 |  | bar | [6 empty] | 165>P>155
| Accumolator 1 Press. |  | MBX09CP501 |  | bar | [6 empty] | 165>P>155
| Accumolator 2 Press. |  | MBX09CP502 |  | bar | [6 empty] | 165>P>155
| Hyd. Oil Temp. |  | MBX01CT501 |  | ºc | [6 empty] | 35<T<60
| Hyd. Tank Level |  | MBX01CL501 |  | L/N/H | [6 empty] | L>%75
| Hyd. Oil Cooling Loop Press. |  | MBX03CP501 |  | bar | [6 empty] | 3.5>P>2.5
| Sound Of Motors |  | - |  | OK | [6 empty] | OK
| Leakage And Cleaning |  | - |  | OK | [6 empty] | OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## FIN FAN SKID
Doc No.: OMSB 008-00 |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS |  | UNIT | Time | [5 empty] | Normal Range
[6 empty] | 0 | 4 | 8 | 12 | 16 | 20
FIN FAN SKID | Pump In Service |  | MPR11AP001 | [8 empty] | 1/2
MPR12AP001
| Pump In Service Suction Press |  | MPR11CP502 |  | bar | [6 empty] | P>0.25
MPR12CP502
| Pump In Service Disch. Press |  | MPR11CP503 |  | bar | [6 empty] | P>3
MPR12CP503
| Tube Bundle 1 Outlet Temp. |  | MPR31CT502 |  | ºc | [6 empty] | 8<T<48
| Tube Bundle 2 Outlet Temp. |  | MPR32CT502 |  | ºc | [6 empty] | 8<T<48
| Water Inlet Cooler Temp. |  | MPR30CT505 |  | ºc | [6 empty] | 10<T<50
| CCW Pump Disch. Temp |  | MPR20CT505 |  | ºc | [6 empty] | 8<T<48
| Pump In Service Strainer DP |  | MPR11CP501 |  | bar | [6 empty] | P<0.35
MPR12CP501
| Surge Tank Level |  | MPR10CL501 |  | OK/NOT OK | [6 empty] | >50%
| Pump Oil Level |  | - |  | OK/NOT OK | [6 empty] | MAX>L>MIN
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## Turbocompressor
Doc No.: OMSB 008-00 |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS |  | UNIT | Time | [5 empty] | Normal Range
[6 empty] | 0 | 4 | 8 | 12 | 16 | 20
Turbocompressor | Flames |  | MBM |  | OK/NOT OK | [6 empty] | OK
| Combustion Chamber Leakage And Sound |  |  |  | OK/NOT OK | [6 empty] | OK
| Turbine Cooling Air |  | MBA21CP501 |  | BAR | [6 empty] | 0.1<P<0.2
| Comp. Air Dryer |  | MBA10AT001 |  | ON/OFF | [6 empty] | ON/OFF
| Leakage And Sound |  | - |  | OK/NOT OK | [6 empty] | OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## OUTDOOR & INDOOR GAS SKID
Doc No.: OMSB 008-00 |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS |  | UNIT | Time | [5 empty] | Normal Range
[6 empty] | 0 | 4 | 8 | 12 | 16 | 20
OUTDOOR & INDOOR GAS SKID | Fuel Gas Duplex Filter In Service |  | EKE11/12AT001/2 |  | 1/2 | [6 empty] | 1/2
| Fuel Gas Duplex Filter In Service ΔP |  | EKE11CP501 |  | bar | [6 empty] | DP<0.35
EKE12CP501
| Fuel Gas Duplex Filter In Service Press. |  | EKE11CP502 |  | bar | [6 empty] | 19<P<22
EKE12CP502
| Fuel Gas Duplex Filter Level |  | EKE11CL501/2 |  | Normal | [6 empty] | NORMAL
EKE12CL501/3
| Line In Service |  | - |  | Main / Bypass | [6 empty] | Main
| Final Chance Filter Pressure |  | EKE30CP502 |  | bar | [6 empty] | 18<P<22
| Final Chance filter DP |  | EKE30CP501 |  | bar | [6 empty] | DP<0.35
| Final Chance Filter Level |  | EKE30CL501 |  | Normal | [6 empty] | %30<L
| Pressure Before Strainer |  | MBP11CP501 |  | bar | [6 empty] | 18<P<22
| Enclosure Fan In Service |  | - |  | 1/2 | [6 empty] | 1/2
| Lighting and Leakage |  | - |  | OK/NOT OK | [6 empty] | OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## AIR INTAKE
Doc No.: OMSB 008-00 |  |  |  | Sabzevar Power plant GT MECHANICAL LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS |  | UNIT | Time | [5 empty] | Normal Range
[6 empty] | 0 | 4 | 8 | 12 | 16 | 20
AIR INTAKE | Leakage And Cleaning |  | _ |  | OK/NOT OK | [6 empty] | OK
| Lighting |  | _ |  | OK/NOT OK | [6 empty] | OK
| Sound |  | _ |  | OK/NOT OK | [6 empty] | OK
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## BBE BUS BAR
Document no: OMSB 002-00 |  |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  |  | UNIT | Time | [5 empty] | Normal Range
[5 empty] | 0 | 4 | 8 | 12 | 16 | 20
BBE BUS BAR | Incoming from unit trans. Voltage |  |  | KV | [6 empty] | 6.4<V<6.7
| Incoming from unit trans .Current |  |  | KA
| BBE BUS Voltage |  |  | KV | [6 empty] | 6.4<V<6.7
| All Local/Remote Selector |  |  | LO/RE | [6 empty] | Remote
| Interconnection to common |  |  | open/close | [6 empty] | CLOSE
| BFT Winding Temp A |  |  | ºc | [6 empty] | T<80
| BFT Winding Temp B |  |  | ºc | [6 empty] | T<80
| BFT Winding Temp C |  |  | ºc | [6 empty] | T<80
| BFT Core TEMP |  |  | ºc | [6 empty] | T<90
| MKC Winding Temp A |  |  | ºc | [6 empty] | T<80
| MKC Winding Temp B |  |  | ºc | [6 empty] | T<80
| MKC Winding Temp C |  |  | ºc | [6 empty] | T<80
| MKC Core TEMP |  |  | ºc | [6 empty] | T<90
| Lamp Test of All Feeders |  |  | OK/NOT OK | [6 empty] | OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## Fuse box
Doc No.: OMSB 007-00 |  |  | Sabzevar power plant GT ELECTRICAL LOG SHEET
Reviw no.0
Date:
DESCRIPTION |  |  |  | UNIT |  | 0 | 4 | 8 | 12 | 16 | 20 | Normal Range
Fuse box | Fuse BOX no.1 |  |  | OPEN/CLOSE | [7 empty] | CLOSE
| Voltage |  |  | V | [7 empty] | 215<V<245
| Current |  |  | A | [7 empty] | I<50
| Fuse BOX no.2 |  |  | OPEN/CLOSE | [7 empty] | CLOSE
| Voltage |  |  | V | [7 empty] | 215<V<245
| Current |  |  | A | [7 empty] | I<50
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## BFE&BME
Doc No.: OMSB 007-00 |  |  | Sabzevar power plant GT ELECTRICAL LOG SHEET
Reviw no.0
Date:
DESCRIPTION |  |  |  | UNIT | 0 | 4 | 8 | 12 | 16 | 20 | Normal Range
BFE&BME LV BUS BAR | BFE INCOMING BREAKER |  |  | open/close | [6 empty] | Close
| BFE Bus Bar Voltage |  |  | V | [6 empty] | 390<V<420
| BFE Incoming Voltage |  |  | V | [6 empty] | 390<V<420
| BFE Incoming Current |  |  | A | [6 empty] | I<500
| BME Bus Bar Voltage |  |  | V | [6 empty] | 390<V<420
| BME Incoming Breaker |  |  | open/close | [6 empty] | Open
| BME Incoming Voltage |  |  | V | [6 empty] | 390<V<420
| BME Incoming Current |  |  | V | [6 empty] | I<250
| BFE/BME Bus tie Current |  |  | A | [6 empty] | I<250
| 220 V DC AVAILABLE |  |  | Yes/No | [6 empty] | Yes
| Local/Remote Selector |  |  | LO/RE | [6 empty] | Remote
| BLS voltage |  |  | V | [6 empty] | 390<V<420
| BLS Current |  |  | A
| BLE voltage |  |  | V | [6 empty] | 390<V<420
| BLE Current |  |  | A
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR | ENGINEER |  | OPERATOR |  | ENGINEER

## Battery Room
Doc No.: OMSB 007-00 |  |  | Sabzevar power plant GT ELECTRICAL LOG SHEET
Reviw no.0
Date:
DESCRIPTION |  |  |  | UNIT | 0 | 4 | 8 | 12 | 16 | 20 | Normal Range
Battery Room | Ventilation fan number in service |  |  | 1 & 2 | [6 empty] | -
| Temp. |  |  | ºc | [6 empty] | 20<T<25
| Level of Battery |  |  | Normal | [6 empty] | min<L<max
| Battery Sulphated |  |  | OK/NOT OK | [6 empty] | OK
| Clraning |  |  | OK/NOT OK | [6 empty] | OK
| Lighting |  |  | OK/NOT OK | [6 empty] | OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR | ENGINEER |  | OPERATOR |  | ENGINEER

## DC UPS
Doc No.: OMSB 007-00 |  |  | Sabzevar power plant GT ELECTRICAL LOG SHEET
Reviw no.0
Date:
DESCRIPTION |  |  |  | UNIT |  | 0 | 4 | 8 | 12 | 16 | 20 | Normal Range
BTL01 BATTERY CHARGER 400VAC/240 VDC | AC input voltage |  |  | V | [7 empty] | 390<V<420
| AC input current |  |  | A | [7 empty] | I<10
| Load voltage |  |  | V | [7 empty] | 215<V<245
| Load current |  |  | A | [7 empty] | 5<I<30
| Battery voltage |  |  | V | [7 empty] | 215<V<245
| Battery current |  |  | A | [7 empty] | 5<I<32
| Charger Status: (Initials;I , Boost:B , Float:F) |  |  | ***** | [7 empty] | Float
| Distribution Of Alarm |  |  | Yes/No | [7 empty] | NO ALARM
BTL02 BATTERY CHARGER 400VAC/240 VDC | AC input voltage |  |  | V | [7 empty] | 390<V<420
| AC input current |  |  | A | [7 empty] | I<10
| Load voltage |  |  | V | [7 empty] | 215<V<245
| Load current |  |  | A | [7 empty] | 5<I<30
| Battery voltage |  |  | V | [7 empty] | 215<V<245
| Battery current |  |  | A | [7 empty] | 5<I<32
| Charger Status: (Initials;I , Boost:B , Float:F) |  |  | ***** | [7 empty] | Float
| Distribution Of Alarm |  |  | Yes/No | [7 empty] | NO ALARM
Inverter | Input DC voltage |  |  | V | [7 empty] | 210<V<245
| Input DC Current |  |  | A | [7 empty] | <95
| Out put Voltage |  |  | V | [7 empty] | 210<V<245
| Output Current |  |  | A
| Out put Frequency |  |  | Hz | [7 empty] | 49<Hz<51
| Fault and Alarm |  |  | OK/NOT OK | [7 empty] | Ok
| Input DC voltage |  |  | V | [7 empty] | 210<V<245
| Input DC Current |  |  | A |  | ` | [5 empty] | <95
| Out put Voltage |  |  | V | [7 empty] | 210<V<245
| Output Current |  |  | A
| Out put Frequency |  |  | Hz | [7 empty] | 49<Hz<51
| Fault and Alarm |  |  | OK/NOT OK | [7 empty] | Ok
BRA | BRA Incomming |  |  | OPEN/CLOSE | [7 empty] | CLOSE
| BRA Voltage |  |  | V
| Fault and Alarm |  |  | OK/NOT OK | [7 empty] | OK
BUB--BUC DISTRIBUTION PANELS | BUB Incoming from BTL01 |  |  | OPEN/CLOSE | [7 empty] | CLOSE
| BUB BUS BAR VOLTAGE |  |  | V | [7 empty] | 210<V<245
| BUS TIE |  |  | OPEN/CLOSE | [7 empty] | CLOSE
| Incoming from BTL 02 |  |  | OPEN/CLOSE | [7 empty] | CLOSE
| BUC BUS BAR VOLTAGE |  |  | V | [7 empty] | 210<V<245
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## CUN
Doc No.: OMSB 007-00 |  |  | Sabzevar power plant GT ELECTRICAL LOG SHEET
Reviw no.0
Date:
DESCRIPTION |  |  |  | UNIT | 0 | 4 | 8 | 12 | 16 | 20 | Normal Range
CUN | Output Voltage CH1 |  |  | V | [6 empty] | >24 V
| Output Current CH1 |  |  | A | [6 empty] | I<25
| Output Voltage CH2 |  |  | V | [6 empty] | >24 V
| Output Current CH2 |  |  | A | [6 empty] | I<25
LCC Status | Lighting |  |  | OK/NOT OK | [6 empty] | OK
| HVAC in Service |  |  | OK/NOT OK | [6 empty] | OK
| Cleaning |  |  | OK/NOT OK | [6 empty] | OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR | ENGINEER |  | OPERATOR |  | ENGINEER

## GATE WAY
Doc No.: OMSB 007-00 |  |  | Sabzevar power plant GT ELECTRICAL LOG SHEET
Reviw no.0
Date:
DESCRIPTION |  | UNIT |  | 0 | 4 | 8 | 12 | 16 | 20 | Normal Range
GATE WAY | GN 6 | R/S | STATUS | [6 empty] | R'¦ 'S' | OK
| GN 7 | R/S | STATUS | [6 empty] | R'¦ 'S' | OK
| GN 8 | R/S | STATUS | [6 empty] | R | OK
| GN 9 | R/S | STATUS | [6 empty] | R | OK
| GN 10 | R/S | STATUS | [6 empty] | R | OK
| GN 11 | R/S | STATUS | [6 empty] | R'¦ 'S' | OK
| GN 12 | R/S | STATUS | [6 empty] | R'¦ 'S' | OK
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## Transformers
Doc No.: OMSB 007-00 |  |  | Sabzevar power plant GT ELECTRICAL LOG SHEET
Reviw no.0
Date:
DESCRIPTION |  |  |  | UNIT | 0 | 4 | 8 | 12 | 16 | 20 | Normal Range
Main Transformer | Main trans. winding temp. HV side |  |  | ºc | [6 empty] | T<100
| Main trans. winding temp. LV side |  |  | ºc | [6 empty] | T<100
| Main trans. Oil temp. |  |  | ºc | [6 empty] | T<80
| Tap Changer Mode (Local/Remote) |  |  | L\R | [6 empty] | Remote
Tap changer position
| Fans Controller (Auto/manual) |  |  | A\M | [6 empty] | AUTO
| Transformer oil level |  |  | OK | [6 empty] | OK
| Tap changer oil level |  |  | OK | [6 empty] | OK
| Sound&Leakage |  |  | OK | [6 empty] | OK
Unit trans | Unit trans. winding temp. |  |  | ºc | [6 empty] | 80
| Unit trans. Oil temp. |  |  | ºc | [6 empty] | 80
| Transformer oil level |  |  | ok/not ok | [6 empty] | OK
| Sound&Leakage |  |  | ok/not ok | [6 empty] | OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR | ENGINEER |  | OPERATOR |  | ENGINEER

## Electrical Fire container
Doc No.: OMSB 006-00 |  |  | SABZEVAR POWER PLANT FIRE FIGHTING LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  |  | KKS | UNIT | time
[6 empty] | 4 | 8 | 16 | 20
ELECTRICAL PMP HOUSE | MV PUMP 1 | OUTLET VLV
PANEL
LINE PRESS
COMMANDER
| MV PUMP 2 | OUTLET VLV
PANEL
LINE PRESS
COMMANDER
| JUCKEY PUMP 1 | OUTLET VLV
PANEL
LINE PRESS
COMMANDER
| JUCKEY PUMP 2 | OUTLET VLV
PANEL
LINE PRESS
COMMANDER
| Accumulator | MAIN VLV
DRAIN VLV
PRESS
| CONTAINER | LIGHT. & VENT. PANEL
FIRE PANEL
LEAKAGE
FAULT & ALARM
CLEANLINESS
RESERVOIR LVL
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## Diesel Pump Container
Doc No.: OMSB 006-00 |  |  | SABZEVAR POWER PLANT FIRE FIGHTING LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  |  | KKS | UNIT | time
[6 empty] | 4 | 8 | 16 | 20
Diesel Pump Container | Diesel Pump PUMP NO.1 | Level of Coolant(water)
Level of oil
Level of fuel (%)
Voltage of Battery no.1
Voltage of Battery no.2
HEATER
Pressure of line
Outlet valve
Auto/Man/Off
Alarm and fault
| Diesel Pump PUMP NO.2 | Level of Coolant(water)
Level of oil
Level of fuel (%)
Voltage of Battery no.1
Voltage of Battery no.2
HEATER
Pressure of line
Outlet valve
Auto/Man/Off
Alarm and fault
| GENERAL CHECK | Fire Panel
Lighting
Ventilation
Cleaness
Level of Water
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## CONTAINER
Doc No.: OMSB 006-00 |  | SABZEVAR POWER PLANT FIRE FIGHTING LOG SHEET
Review no.0
Date:
DESCRIPTION |  |  | KKS | UNIT | time
[5 empty] | 4 | 8 | 16 | 20
OUT DOOR CHECK | Hydraunt outlet Valve
Level of Water
Pressure discharge line
Lighting
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR | ENGINEER

## MV BUS BCA BCB
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
MV BUS BCA/BCB | BCA BUS BAR Voltage |  | KV | [6 empty] | 6.4<V<6.8
| BCB BUS BAR Voltage |  | KV | [6 empty] | 6.4<V<6.8
| BUS TIE |  | Open / Close | [6 empty] | OPEN
| Bus Tie Lock Out Relay |  | Set / Reset | [6 empty] | Reset
| INCOMING FROM UNIT 1 |  | Open / Close | [6 empty] | CLOSE
| Incoming 1 Lock Out Relay |  | Set / Reset | [6 empty] | Reset
| Incoming 1 Earth Switch |  | OPEN/CLOSE | [6 empty] | Open
| Current of Incoming 1 |  | A(sepam)
| Voltage of Incoming 1 |  | V(sepam) | [6 empty] | 6.4<V<6.8
| INCOMING FROM UNIT 2 |  | Open / Close | [6 empty] | CLOSE
| REMOTE POS FOR BUS TIE |  | R/L | [6 empty] | R
| Lamp Test OF All Feeders |  | OK/Not OK | [6 empty] | ok
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## BUB BUC
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
Rectifire 400Vac/220Vdc (Battery Charger) | BTL01 | AC Input Voltage | V | [6 empty] | 380<V<420
|  | AC Input Current | A
|  | Input Frequency | Hz | [6 empty] | 49<F<51
|  | Charge Voltage | V | [6 empty] | 210<V<245
|  | Charge Current | A
|  | Load Voltage | V
|  | Charger Status: (Initials; Boost:Float) | ** | [6 empty] | Auto/Float
|  | Fault and alarm | OK/Not OK
|  | Lamp test | OK/Not OK
| BTL02 | AC Input Voltage | V | [6 empty] | 380<V<420
|  | AC Input Current | A
|  | Input Frequency | Hz | [6 empty] | 49<F<51
|  | Rec. Voltage | V | [6 empty] | 210<V<245
|  | Rec. Current | A
|  | Load Voltage | V
|  | Charger Status: (Initials; Boost:Float) | ** | [6 empty] | Auto/Float
|  | Fault and alarm | OK/Not OK
|  | Lamp test | OK/Not OK
BUB/BUC | BUB | BUB load Voltage | V
|  | BUB load Current | A
| BUC | BUB load Voltage | V
|  | BUB load Current | A
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## Inverter 220Vdc 220Vac
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
Inverter 220Vdc/220Vac | Inverter no.1 | Dc input Voltage | V | [6 empty] | 210<V<245
|  | Dc input Current | A | [6 empty] | < 95
|  | Inverter Voltage | V | [6 empty] | 210<V<245
|  | Inverter Current | A
|  | Inverter Frequency | Hz | [6 empty] | 49<F<51
|  | Lamp test | OK/Not OK
|  | Fault and alarm | OK/Not OK
| Inverter no.2 | Dc input Voltage | V | [6 empty] | 210<V<245
|  | Dc input Current | A | [6 empty] | < 95
|  | Inverter Voltage | V | [6 empty] | 210<V<245
|  | Inverter Current | A
|  | Inverter Frequency | Hz | [6 empty] | 49<F<51
|  | Lamp test | OK/Not OK
|  | Fault and alarm | OK/Not OK
BRA/B 220 V ac |  | BRA Voltage | V | [6 empty] | 210<V<250
|  | BRA Current | A
|  | BRB Voltage | V
|  | BRB Current | A | [6 empty] | 210<V<250
|  | By Pass Voltage | V | [6 empty] | 210<V<250
|  | static switch 1/2 by pass | 1 OR 2 | [6 empty] | 1
|  | fault and alarm | OK/Not OK | [6 empty] | ok
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## LV BUS
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
LV BUS BHA/BHB | Incoming From BHT01 |  | Open / Close | [6 empty] | CLOSE
| BHA Incoming Voltage |  | V | [6 empty] | 380<V<420
| BHA Bus Voltage |  | V | [6 empty] | 380<V<420
| BHA Incoming Current |  | A
| Incoming 1 TCS & Lock Out |  | OK/Not OK | [6 empty] | Ok
| BHA Incoming DC Healthy |  | OK/Not OK | [6 empty] | Ok
| BUS TIE |  | Open / Close | [6 empty] | OPEN
| LOCAL/REMOTE Selector |  | L / R | [6 empty] | Remote
| Incom. From BHT02 |  | Open / Close | [6 empty] | Close
| BHB Incoming Voltage |  | V | [6 empty] | 380<V<420
| BHB Bus Voltage |  | V | [6 empty] | 380<V<420
| BHB Incoming Current |  | A
| Incoming 2 TCS & Lock Out |  | OK/Not OK | [6 empty] | ok
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## LV EMERGENCY BUS BAR
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
BMC BUS BAR | Energized From INCOMING 1/2 |  | 1/2
| Incoming 1 Voltage(BHA) |  | V | [6 empty] | 380<V<420
| Incoming 2 Voltage(BMA) |  | V | [6 empty] | 380<V<420
| AUTO/MANUAL Selector |  | A/M | [6 empty] | AUTO
LV EMERGENCY BUS BAR BMA / BMB | incoming from BHA |  | Open / Close | [6 empty] | close
| BMA incoming voltage |  | V | [6 empty] | 380<V<420
| BMA bus voltage |  | V | [6 empty] | 380<V<421
| BMA incoming current |  | A
| Incom. From BHB |  | Open / Close | [6 empty] | close
| BMB incoming voltage |  | V | [6 empty] | 380<V<420
| BMB BUS voltage |  | V | [6 empty] | 380<V<421
| BMB incoming current |  | A
| LOCAL/REMOTE Selector |  | L / R | [6 empty] | Remote
| Fault and alarm |  | OK/Not OK
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## Battery
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
Battery | Set1 | Battery voltage -set1 | V | [6 empty] | -
|  | Battery current-set1 | A | [6 empty] | -
| Set2 | Battery voltage -set2 | V | [6 empty] | -
|  | Battery current-set2 | A | [6 empty] | -
| Room | ventilaton fan is in service | OK/Not OK | [6 empty] | ok
|  | Battery sulphated | OK/Not OK | [6 empty] | ok
|  | Temp | ◦C
|  | Level of water | OK/Not OK | [6 empty] | ok
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## DG
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
DG | DG1 | DG mode(Local panel) | Auto/Manual | [6 empty] | Auto
|  | DG mode(8610) | Auto/Manual | [6 empty] | Auto
|  | Battery voltage | V | [6 empty] | 26<V<28
|  | coolant temp | ** | [6 empty] | >34
|  | Level of fuel | OK/Not OK | [6 empty] | ok
|  | Leakage | OK/Not OK | [6 empty] | ok
| DG2 | DG mode(Local panel) | Auto/Manual | [6 empty] | Auto
|  | DG mode(8610) | Auto/Manual | [6 empty] | Auto
|  | Battery voltage | V | [6 empty] | 26<V<29
|  |  | ** | [6 empty] | >35
|  | Level of fuel | OK/Not OK | [6 empty] | ok
|  | Leakage | OK/Not OK | [6 empty] | ok
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## BHT TRANS
Document no: OMSB 002-00 |  | Sabzevar power plant CCB Switchgear LOGSHEET
Review no: 0
Date:
DESCRIPTION |  |  | UNIT | 0:00 | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | Norm Range
BHT TRANS | BHT01 | Oil Temp | **
|  | Conservator Level | %
|  | Leakage & Sound | OK/Not OK
| BHT02 | Oil Temp | **
|  | Conservator Level | %
|  | Leakage & Sound | OK/Not OK
NIGHT SHIFT |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## CUN-P 01
DOC. NO: OMSB 004-00 |  |  | SABZEVAR POWER PLANT ES & SCADA
REV. NO:0
DATE:
DESCRIPTION |  |  | UNIT | 00:00 | 04:00 | 08:00 | 12:00 | 16:00 | 20:00 | NORM. RANGE
RECTIFIRE 400VAC/52VDC | LOAD VOLT. |  | V
| INPUT VOLT. |  | V
| CHARGER STATUS |  | I, B, F
| FAULT & ALARM |  | OK, NOK
| LOAD VOLT. |  | V
| INPUT VOLT. |  | V
| CHARGER STATUS |  | I, B, F
| FAULT & ALARM |  | OK, NOK
BUA01 | INC. 1 VOLT. |  | V
| BUS-BAR 1 VOLT. |  | V
| BUS-BAR 1 CURR. |  | A
| INC. 2 VOLT. |  | V
| BUS-BAR 2 VOLT. |  | V
| BUS-BAR 2 CURR. |  | A
| SELECTOR PANEL |  | A, M
CUN01 | VOLTAGE 1 |  | V
| CURRENT 1 |  | A
| VOLTAGE 2 |  | V
| CURRENT 2 |  | A
| POWER SUPPLY |  | 1 & 2 | [6 empty] | 1 & 2 MUST BE OK.
CUP01 | VOLTAGE 1 |  | V
| CURRENT 1 |  | A
| VOLTAGE 2 |  | V
| CURRENT 2 |  | A
| POWER SUPPLY |  | 1, 2 | [6 empty] | 1 OR 2 MUST BE OK.
NIGHT SHIFT |  |  |  |  | DAY SHIFT |  |  |  | NIGHT SHIFT
OPERATOR |  | ENGINEER |  |  | OPERATOR |  | ENGINEER |  | OPERATOR |  | ENGINEER

## ROOM
DOC. NO: OMSB 004-00 |  | SABZEVAR POWER PLANT ES & SCADA
REV. NO:0
DATE:
DESCRIPTION |  |  | UNIT | 00:00 | 04:00 | 08:00 | 12:00 | 16:00 | 20:00 | NORM. RANGE
SCADA | ROOM TEMPERATURE |  | °C | [6 empty] | 22-24 °C
| BUS-BAR TEMPERATURE |  | °C | [6 empty] | 22-24 °C
ES | ROOM TEMPERATURE |  | °C | [6 empty] | 22-24 °C
CCR | ROOM TEMPERATURE |  | °C | [6 empty] | 22-24 °C
Night shift1 |  |  | Day shift |  |  |  | Night shift2
OPERATOR | Engineer |  | OPERATOR |  | Engineer |  | OPERATOR |  | Engineer

## source
OK | 1 | REMOTE | NORMAL | ON | Main | OPEN | امیرفواد استیری | محمد عطاردی | R | AUTO | LOW | SET | Float | OP
NOT OK | 2 | LOCAL | NOT NORMAL | OFF | Bypass | CLOSE | حامد صباغ زاده | امین اسحاقی نیا | S | MANUAL | HIGH | RESET | Boost | TG
[7 empty] | مهرداد زارع | سعید منصوری |  | OFF | NORMAL |  | Initials | SS
[7 empty] | مهدی بروجردی | حسن چوپانی
رضا افشاردوست
مهدی ملوندی
امیرفواد استیری
حامد صباغ زاده
مهرداد زارع
مهدی بروجردی